H2SMARTTM

Modbus RTU Interface Via RS-485
Modbus RTU інтерфейс по RS-485

Version 6
H2Smart Modbus RTU Interface Via RS-485 – Rev. 6	Page 2 of 6

Manual #: 005

Rev No: 6
Date: 02 April 2015

THIS MANUAL IS SUPPLIED IN ONE (1) COPY.
ЦЯ ІНСТРУКЦІЯ ПОСТАЧАЄТЬСЯ В ОДНОМУ (1) ПРИМІРНИКУ.

COPYRIGHT(C)

No part of this publication may be duplicated, copied, and/or transmitted without the prior written permission of United Process Controls.

The information contained in this document is STRICTLY CONFIDENTIAL and PROPRIETARY to United Process Controls, and shall not be: i) reproduced or disclosed in part or in whole, ii) used for any design or manufacturing of heat treating and/or control equipment, or any other purpose except for that which it is supplied under the terms of the Contract, unless the express written authorization is obtained from United Process Controls.

Drawings and photographs included in the documentation are the property of United Process Controls, and it is strictly forbidden to reproduce them, transmit them to a third party, or use them for manufacturing and/or design of equipment. Sub-licensing of any technical information contained in this Documentation is strictly forbidden under the terms of the Contract.

United Process Controls reserves the right to modify this document without prior notice.

WARRANTY:

United Process Controls (UPC) warrants its goods as being free of defective materials and faulty workmanship. Contact your local sales office for warranty information. If warranted goods are returned to UPC during the period of coverage, UPC will repair or replace without charge those items it finds defective. The foregoing is Buyer's sole remedy and is in lieu of all other warranties, expressed or implied, including those of merchantability and fitness for a particular purpose. Specifications may change without notice. The information we supply is believed to be accurate and reliable as of this printing. However, we assume no responsibility for its use.

CE Conformity (Europe)

This product conforms to 73/23/EEC, the Low Voltage Directive, and 89/336/EEC, the EMC Directive.

AMS Conformity (North America)

This product conforms to SAE Aerospace Material Specifications AMS 2759/10 for nitriding and 2759/12 for nitrocarburizing

For assistance please contact:	United Process Controls Inc.
TEL: +1 513 772 1000 • FAX: +1 513 326 7090 Toll-Free North America +1-800-547-1055 upc.support@group-upc.com
www.group-upc.com

Copyright © 2014, Marathon Monitors Inc., a member of United Process Controls.	All rights to copy, reproduce and transmit are reserved.
H2Smart Modbus RTU Interface Via RS-485 – Rev. 6	Page 3 of 6

TABLE OF CONTENTS

1.	GENERAL................................................................................................................................................... 4

2.	MODBUS REGISTER ASSIGNMENT ............................................................................................................. 4
2.1 READ ONLY REGISTERS..........................................................................................................................................4 2.2 READ/WRITE REGISTERS........................................................................................................................................5

Copyright © 2014, Marathon Monitors Inc., a member of United Process Controls.	All rights to copy, reproduce and transmit are reserved.
H2Smart Modbus RTU Interface Via RS-485 – Rev. 6	Page 4 of 6

1. General Загальний опис

H2SmartTM supports the standard Modbus commands 3 (Read n registers), 6 (write one register), 7 (fast read of sampling enable status). Floating point values are converted to and from 16 bit integers for Modbus communication, providing a LSB value given in the register assignment below. For example, if the H2SmartTM is calibrated for dissociation, a value of 5000 read from Modbus register 0 means a measured dissociation of 50.00%.
H2SmartTM підтримує стандартні команди Modbus 3 (читати n регістрів), 6 (записувати один регістр), 7 (швидке читання статусу дозволу вибірки). Значення з плаваючою комою перетворюються на 16-розрядні цілі числа та з них для зв’язку Modbus, забезпечуючи значення LSB, наведене у призначенні регістрів нижче. Наприклад, якщо H2SmartTM відкалібровано на дисоціацію, значення 5000, зчитане з реєстру Modbus 0, означає виміряну дисоціацію 50,00%

Any standard Modbus master with freely settable data addresses should be able to communicate with H2SmartTM without any problems. The interface must be configured for 4 wire communication. (Future development is planned for 2 wire communication.) The connection is through the female DB9 connector
on the front of the unit designated 'Opt. Interface'

DB9 RS485 pin assignment

1 - A (TX-) (four wire mode only)	(WHT) 2 + B (TX+)(four wire mode only)	(BLK) 3 +B (RX/TX+)	(BLK)
5 GND (Must be connected)	(GND) 8 - A (RX/TX-) (RED)

(note: 2 wire not currently supported)
according to the table. The default Modbus slave address of the unit is 2. The H2SmartTM is shipped with default parameters of 9600Bd, 8 bits/character, parity even, 1 stop bit. Setup of Modbus device address and interface mode is done using the H2SmartTM service software.

2. Modbus Register Assignment

2.1 Read Only Registers

0	H2SmartTM sensor result (H2 or Dissociation, depending on calibration type) in 0.01% 1	Flow rate in 0.001 SLM or CFH (depending on flow sensor unit configuration)
3	TBlock in 0.01°C or °F (depending on temperature unit configuration) 4	Taux in 0.01°C or °F (depending on temperature unit configuration)
5	State of the digital inputs 6	State of the digital outputs
28	Model calculated KN in units of 0.01 29	Model caluclated aC in units of 0.001
37	O2 probe voltage measured by the optional O2 probe input module in 0.1mV
38	O2 probe temperature of the O2 input module in 0.1 °C or ° F (depending on temperature unit configuration)
48	Model calculated KC in units of 0.01

Copyright © 2014, Marathon Monitors Inc., a member of United Process Controls.	All rights to copy, reproduce and transmit are reserved.
H2Smart Modbus RTU Interface Via RS-485 – Rev. 6	Page 5 of 6

2.2 Read/Write Registers

9	Modbus sampling enable override signal: 0: Sampling stopped, 1: Sampling enabled
For continuous sampling, the sampling enable signal must be sent regularly every 10 to 80 seconds. If the sampling enable signal is not received, the sampling will stop after 90 seconds. This is to ensure that the unit does not get damaged in the event of a loss of communication.
10	Process gas 1 (Nitrogen) flow value in 0.001 m3/h (must be updated for a correct KN calculation) 11	Process gas 2 (Ammonia) flow value in 0.001 m3/h (must be updated for a correct KN calculation) 12	Process gas 3 (Dissociated Ammonia) flow value in 0.001 m3/h (must be updated for a correct KN
calculation)
13	Process gas 4 (Carbon Dioxide) flow value in 0.001 m3/h (must be updated for a correct KN calculation)
14	Process gas 4 (Carbon Monoxide) flow value in 0.001 m3/h (must be updated for a correct KN calculation)
18	Furnace model Initialize. Writing 1 to this value resets the furnace model to the start condition. 30	Furnace temperature in 0.01°C

Copyright © 2014, Marathon Monitors Inc., a member of United Process Controls.	All rights to copy, reproduce and transmit are reserved.
H2Smart Modbus RTU Interface Via RS-485 – Rev. 6	Page 6 of 6

Reach us at www.group-upc.com

United Process Controls brings together leading brands to the heat treating industry including Waukee Engineering, Furnace Control, Marathon Monitors and Process-Electronic.
We provide prime control solutions through our worldwide sales and services network with easy-to-access local support.

UNITED PROCESS CONTROLS INC. MARATHON MONITPORS PLANT

8904 Beckett Rd., West Chester, OH 45069 USA

Phone: +1-513-772-1000 Fax: +1-513-326-7090 E-mail: upc.sales@group-upc.com

Copyright © 2014, Marathon Monitors Inc., a member of United Process Controls.	All rights to copy, reproduce and transmit are reserved.